## Sheet1
| Volts A-N | Volts B-N | Volts C-N | Volts A-B | Volts B-C | Volts C-A | Amps A | Amps B | Amps C | Power | VAR | VA | Power Factor | Frequency | Energy - Recv'd | Energy - Delv'd | Energy - Netq | Energy - Total | VAR-hrs - Pos | VAR-hrs - Neg | VAR-hrs - Net | VAR-hrs - Total | VA-hrs - Total
| Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | Float | SINT32 | SINT32 | SINT32 | SINT32 | SINT32 | SINT32 | SINT32 | SINT32 | SINT32
| 1000 | 1002 | 1004 | 1006 | 1008 | 1010 | 1012 | 1014 | 1016 | 1018 | 1020 | 1022 | 1024 | 1026 | 1100 | 1102 | 1104 | 1106 | 1108 | 1110 | 1112 | 1114 | 1116
0 | 279.5 | 266.5 | 286.9 |  |  |  | 377.8 | 384.9 | 377.8 | 318565.9 |  | 319939 | 0.98868 | 59.27 |  |  |  | 53222
1 | 281.8 | 268.7 | 289.4 |  |  |  | 399.8 | 407.4 | 400.2 | 336996.1 |  | 338355.9 | 0.99799 | 59.78 |  |  |  | 53306
2 | 280.8 | 269.2 | 288.9 |  |  |  | 410.4 | 418 | 410.8 | 345157.6 |  | 346429 | 0.99802 | 59.77 |  |  |  | 53392
3 | 280.6 | 269.2 | 288.8 |  |  |  | 420.7 | 428.5 | 420.8 | 354262.7 |  | 354909 | 0.99839 | 59.8 |  |  |  | 53481
4 | 281.6 | 269.5 | 289 |  |  |  | 435.5 | 443.2 | 435.7 | 366548.7 |  | 368141 | 0.99771 | 59.97 |  |  |  | 53573
5 | 281.2 | 269 | 289.5 |  |  |  | 444.9 | 452.9 | 445.4 | 374980.5 |  | 376204.4 | 0.99684 | 59.96 |  |  |  | 53666
6 | 280.1 | 269.5 | 289.4 |  |  |  | 454.9 | 462.3 | 454.8 | 381942.3 |  | 383842 | 0.99583 | 59.96 |  |  |  | 53762
7 | 280.2 | 269.6 | 289.4 |  |  |  | 461.7 | 469.3 | 461.8 | 387862.5 |  | 389445.2 | 0.99521 | 60.19 |  |  |  | 53859
8 | 280.4 | 269.7 | 289 |  |  |  | 465.5 | 473 | 465.7 | 391273.4 |  | 392839.4 | 0.99485 | 60.14 |  |  |  | 53957
9 | 280 | 269.5 | 287.7 |  |  |  | 469.3 | 477.1 | 470 | 393965 |  | 395738.9 | 0.99446 | 60.06 |  |  |  | 54055
10 | 281.3 | 270.3 | 288.1 |  |  |  | 470.2 | 477.8 | 470.8 | 395476.6 |  | 397388.8 | 0.99434 | 59.94 |  |  |  | 54154

## Sheet2
Firmware (Do Not Edit) |  |  | Manufacturer's Information | [6 empty] | Firmware Conversion |  |  |  | Firmware (Do Not Edit) | [9 empty] | Old Firmware
Index | Variable Name | Units | Variable Name | Units | Function Code | Starting Reg | # of Regs | Reg Type | Multiplier/ Scalar | Query Index | Reg Offset | Multiplier/ Scaler | Comments | Function Code | Starting Reg | # of Regs | Reg Type | Multiplier/Scalar | Variable Type | Table Processing | Table Data Type | Polling Interval | Data Refresh Interval | Variable Name |  |  | Units
1 | mtr_comm_code | [17 empty] | Long | Sample | Long | Every Poll | Never | result_PEM | result_UEM | result_LEM
2
102 | mtr_sn |  | Meter Serial Number |  | 3 | 9 | 8 | ASCII | 1 | every: 5 | 0 |  |  | 3 | 9 | 8 | ASCII |  | String * 40 | Sample | String | Every Poll | Never | SN_PEM
103 | mtr_fw_ver |  | Firmware Version |  | 3 | 18 | 2 | ASCII | 1 | daily: 1 | 0 |  |  | 3 | 18 | 2 | ASCII |  | String * 40 | Sample | String | Daily | Daily
104 | mtr_map_ver |  | Map Version |  | 3 | 20 | 1 | UINT16 | 1 | daily: 1 | 0 |  |  | 3 | 20 | 1 | UINT16 |  | String * 40 | Sample | String | Daily | Daily
105 | mtr_config |  | Meter Configuration |  | 3 | 21 | 1 | UINT16 | 1 | daily: 1 | 0 |  | lowest 6 bits: indicates calibration frequency | 3 | 21 | 1 | UINT16 |  | String * 64 | Sample | String | Daily | Daily
4 | mtr_ac_voltage_an | Volts | Volts A-N | volts | 3 | 1000 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1000 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_AN_PEM | Vac_AN_UEM | Vac_AN_LEM | Vac
5 | mtr_ac_voltage_bn | Volts | Volts B-N | volts | 3 | 1002 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1002 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_BN_PEM | Vac_BN_UEM | Vac_BN_LEM | Vac
6 | mtr_ac_voltage_cn | Volts | Volts C-N | volts | 3 | 1004 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1004 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_CN_PEM | Vac_CN_UEM | Vac_CN_LEM | Vac
7 | mtr_ac_voltage_ab | Volts | Volts A-B | volts | 3 | 1006 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1006 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_AB_PEM | Vac_AB_UEM | Vac_AB_LEM | Vac
8 | mtr_ac_voltage_bc | Volts | Volts B-C | volts | 3 | 1008 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1008 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_BC_PEM | Vac_BC_UEM | Vac_BC_LEM | Vac
9 | mtr_ac_voltage_ca | Volts | Volts C-A | volts | 3 | 1010 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1010 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Vac_CA_PEM | Vac_CA_UEM | Vac_CA_LEM | Vac
12 | mtr_ac_current_a | Amps | Amps A | amps | 3 | 1012 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1012 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Iac_A_PEM | Iac_A_UEM | Iac_A_LEM | Aac
13 | mtr_ac_current_b | Amps | Amps B | amps | 3 | 1014 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1014 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Iac_B_PEM | Iac_B_UEM | Iac_B_LEM | Aac
14 | mtr_ac_current_c | Amps | Amps C | amps | 3 | 1016 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1016 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Iac_C_PEM | Iac_C_UEM | Iac_C_LEM | Aac
17 | mtr_ac_power | Watts | Watts, 3-Ph total | watts | 3 | 1018 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1018 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Pac_PEM | Pac_UEM | Pac_LEM | W
27 | mtr_ac_vars | VARs | VARs, 3-Ph total | VARs | 3 | 1020 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1020 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | VARac_PEM | VARac_UEM | VARac_LEM | VAR
23 | mtr_ac_va | VAs | VAs, 3-Ph total | VAs | 3 | 1022 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1022 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | VAac_PEM | VAac_UEM | VAac_LEM | VA
31 | mtr_ac_pf |  | Power Factor, 3-Ph total |  | 3 | 1024 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1024 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | PFac_PEM | PFac_UEM | PFac_LEM
35 | mtr_ac_freq | Hz | Frequency | Hz | 3 | 1026 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1026 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Fac_PEM | Fac_UEM | Fac_LEM | Hz
15 | mtr_ac_current_n | Amps | Neutral Current | amps | 3 | 1028 | 2 | FLOAT | 1 | every: 1 | -1 |  |  | 3 | 1028 + -1 | 2 | FLOAT |  | Float | Average | IEEE4 | Every Poll | Every Poll | Iac_N_PEM | Iac_N_UEM | Iac_N_LEM | Aac
36 | mtr_ac_energy_rcvd | kWh | W-hours, Received | kWh | 3 | 1100 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1100 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never | Eac_Total_Delv_PEM | Eac_Total_Delv_UEM | Eac_Total_Delv_LEM | kWh
37 | mtr_ac_energy_delv | kWh | W-hours, Delivered | kWh | 3 | 1102 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1102 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never | Eac_Total_Rcvd_PEM | Eac_Total_Rcvd_UEM | Eac_Total_Rcvd_LEM | kWh
38 | mtr_ac_energy_net | kWh | W-hours, Net | kWh | 3 | 1104 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1104 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never
39 | mtr_ac_energy_total | kWh | W-hours, Total | kWh | 3 | 1106 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1106 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never
58 | mtr_ac_var_hrs_pos | kVARh | VAR-hours, Positive | kVARh | 3 | 1108 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1108 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never | kVARh_Total_Pos_PEM | kVARh_Total_Pos_UEM | kVARh_Total_Pos_LEM | kVARh
59 | mtr_ac_var_hrs_neg | kVARh | VAR-hours, Negative | kVARh | 3 | 1110 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1110 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never | kVARh_Total_Neg_PEM | kVARh_Total_Neg_UEM | kVARh_Total_Neg_LEM | kVARh
62 | mtr_ac_var_hrs_net | kVARh | VAR-hours, Net | kVARh | 3 | 1112 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1112 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never
63 | mtr_ac_var_hrs_total | kVARh | VAR-hours, Total | kVARh | 3 | 1114 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1114 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never
51 | mtr_ac_va_hrs_total | kVAh | VA-hours, Total | kVAh | 3 | 1116 | 2 | SINT32 | 1 | every: 2 | 0 |  |  | 3 | 1116 | 2 | SINT32 |  | Float | Sample | IEEE4 | Every Poll | Never | kVAh_Total_PEM | kVAh_Total_UEM | kVAh_Total_LEM | kVAh
74 | mtr_ac_current_a_angle | Deg | Phase A Current | degree | 3 | 4100 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4100 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Ia_PEM | Angle_Ia_UEM | Angle_Ia_LEM | deg
75 | mtr_ac_current_b_angle | Deg | Phase B Current | degree | 3 | 4101 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4101 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Ib_PEM | Angle_Ib_UEM | Angle_Ib_LEM | deg
76 | mtr_ac_current_c_angle | Deg | Phase C Current | degree | 3 | 4102 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4102 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Ic_PEM | Angle_Ic_UEM | Angle_Ic_LEM | deg
70 | mtr_ac_voltage_ab_angle | Deg | Angle, Volts A-B | degree | 3 | 4103 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4103 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Vab_PEM | Angle_Vab_UEM | Angle_Vab_LEM | deg
71 | mtr_ac_voltage_bc_angle | Deg | Angle, Volts B-C | degree | 3 | 4104 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4104 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Vbc_PEM | Angle_Vbc_UEM | Angle_Vbc_LEM | deg
72 | mtr_ac_voltage_ca_angle | Deg | Angle, Volts C-A | degree | 3 | 4105 | 1 | SINT16 | 0.1 | every: 3 | 0 |  |  | 3 | 4105 | 1 | SINT16 | 0.1 | Float | Sample | IEEE4 | Every Poll | Every Poll | Angle_Vca_PEM | Angle_Vca_UEM | Angle_Vca_LEM | deg
107 | mtr_ac_ct_ratio |  | CT multiplier & denominator, CT numerator |  | 3 | 30000 | 2 | UINT16 | 1 | daily: 2 | 0 |  | ct_mult * ct_numer : ct_denom (see manual pg 129 for bit mapping) | 3 | 30000 | 2 | UINT16 |  | String * 20 | Sample | String | Daily | Daily | CT_Numer_PEM
109 | mtr_ac_pt_ratio |  | PT numerator, PT denominator |  | 3 | 30002 | 3 | UINT16 | 1 | daily: 2 | 0 |  | pt_mult * pt_numer : pt_denom (see manual pg 129 for bit mapping) | 3 | 30002 | 3 | UINT16 |  | String * 20 | Sample | String | Daily | Daily
106 | mtr_ac_config |  | PT multiplier & hookup |  | 3 | 30004 | 1 | UINT16 | 1 | daily: 2 | 0 |  | lowest 4 bits: 0 = 3wye, 1 = delta, 3 = 2.5wye | 3 | 30004 | 1 | UINT16 |  | String * 20 | Sample | String | Daily | Daily
105 | mtr_config |  | Power & Energy Format |  | 3 | 30006 | 1 | UINT16 | 1 | daily: 2 | 0 |  | bits 0-2: energy decimal places, bits 4-6: energy scale | 3 | 30006 | 1 | UINT16 |  | String * 64 | Sample | String | Daily | Daily
105 | mtr_config |  | User Settings Flags |  | 3 | 30015 | 1 | UINT16 | 1 | daily: 3 | 0 |  | bit 1: power factor sign flipped, bit 2: 1 = view as generator, 0 = view as load | 3 | 30015 | 1 | UINT16 |  | String * 64 | Sample | String | Daily | Daily
90 | mtr_fault_01 |  | System Sanity Indicator |  | 3 | 40001 | 1 | UINT16 | 1 | every: 4 | 0 |  | see faults sheet | 3 | 40001 | 1 | UINT16 |  | Long | Sample | UINT4 | Every Poll | 15 Minute
21 | mtr_ac_power_rcvd | Watts | Watts, 3-Ph total | watts | 3 |  |  |  |  | every: 1 |  |  | power_rcvd = if power < 0 then abs(power) else 0 | 3 |  |  |  |  | Float | Average | IEEE4 | Every Poll | Every Poll |  | Pnet_Rcvd |  | W
22 | mtr_ac_power_delv | Watts | Watts, 3-Ph total | watts | 3 |  |  |  |  | every: 1 |  |  | power_delv = if power > 0 then abs(power) else 0 | 3 |  |  |  |  | Float | Average | IEEE4 | Every Poll | Every Poll |  | Pnet_Delv |  | W

## Sheet3
SN1 | SN2 | SN3 | SN4 | SN5 | SN6 | SN7 | SN8 | FW1 | FW2 | Map Ver | CFG | Volts | Volts | Volts | Volts | Volts | Volts | Amps | Amps | Amps | Watts | VARs | VAs | PF | Hz | Amps | kWh | kWh | kWh | kWh | kVARh | kVARh | kVARh | kVARh | kVAh | Deg | Deg | Deg | Deg | Deg | Deg | CT | PT | PT M&H | P&E F | SET FLAG | Sys San
UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | FLOAT | SIN32 | SIN32 | SIN32 | SIN32 | SIN32 | SIN32 | SIN32 | SIN32 | SIN32 | SINT16 | SINT16 | SINT16 | SINT16 | SINT16 | SINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16 | UINT16
9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 18 | 19 | 20 | 21 | 1000 | 1002 | 1004 | 1006 | 1008 | 1010 | 1012 | 1014 | 1016 | 1018 | 1020 | 1022 | 1024 | 1026 | 1028 | 1100 | 1102 | 1104 | 1106 | 1108 | 1110 | 1112 | 1114 | 1116 | 4100 | 4101 | 4102 | 4103 | 4104 | 4105 | 30000 | 30002 | 30004 | 30006 | 30015 | 40001
13621 | 13364 | 13872 | 12852 | 8224 | 8224 | 8224 | 2 | 12336 | 12597 | 34 | 1340 | 120 | 120 | 120 | 120 | 120 | 120 | 10 | 10 | 10 | 100 | 1 | 5 | 1 | 60 | 0 | 1500 | 250 | 1250 | 1750 | 900 | 100 | 150 | 700 | 200 | 120 | 120 | 120 | 120 | 120 | 120 | 1200 | 120 | 3841 | 255 | 0 | 0